## Inputs
Phase 2 Load Calc Workbook (MOCK)
Project | EV Charging Site Project
Site | Place (Palo Alto, CA) (mock)
Code basis (mock) | 2022 CEC; NEC concepts referenced (mock)
EVSE model (basis) | ElectriCharge L2-7.6-G (revA)
EVSE ports | 8
EVSE continuous current per port (A) | 32
Continuous load factor | 1.25
Unmanaged EV feeder current (A) | 320 | 8 * (32 * 1.25)
Service headroom (A) (from screening) | 250 | From Phase 0 screening (mock)
Decision constraint | Avoid service upgrade unless unavoidable

## LoadCalc
Load Calc (mock excerpt)
Item | Value | Units | Notes
Ports | 8 | ea | Program intent basis
I_cont per port | 32 | A | From EVSE cut sheet (revA, mock)
Continuous factor | 1.25 | - | Per continuous-load treatment (mock)
I_design per port | 40 | A | 32 * 1.25
I_unmanaged total | 320 | A | 8 * 40
Headroom available | 250 | A | Service utilization basis (mock)
Deficit (unmanaged) | -70 | A | 250 - 320
Managed cap target | 250 | A | EMS setpoint basis (mock)
Feeder OCPD (selected) | 350 | A | Mock selection
EV subpanel bus (selected) | 400 | A | Mock selection

## Summary
Summary (mock)
Outcome | Unmanaged exceeds headroom; EMS required
Key numbers
Unmanaged EV current | 320 A | 8 ports @ 32A cont, 125%
Headroom basis | 250 A | screening (mock)
Required measure | Listed EMS to cap ≤250A | architecture decision input
Downstream use | P3 one-line, notes, schedules; P6 utility letter